ARECIBO OBSERVATORY

SERVO DRIVE SYSTEM UPGRADE

Volume II - Section 3

OPERATION AND MAINTENANCE MANUAL

CONTROL SYSTEMS


Programmable Controller Siemens Simatic S5-135U

DESCRIPTION OF INTERNAL INTERFACES

Provided for

National Astronomy and Ionosphere Center
Cornell University

Ithaca, NY, USA

Project No. 10/95034
Rev.: 2.3
December 1999

| Vertex Antennentechnik GmbH Baumstr. 50 47198 Duisburg Germany Tel. +49-2066-2096-0; Fax -11 | Vertex Communications Corporation 2600 Longview Street Kilgore, TX 75663 U.S.A. Tel. 903-984-0555; Fax -1826 |
| --- | --- |

Contents

1. GENERAL INFORMATION

1.1. Foreword

1.2. Interface List

2. INTERFACE CPU 928  -  CP 581

2.1. Transfer Requirements

2.2. Description of Protocols

2.2.1. From CPU to CP 581

2.2.2. From CP 581 to CPU

2.3. Data Formats

2.4. Format of Individual Bytes

3. INTERFACE TO PCU

3.1. Hardware

3.2. Transfer Requirements

3.3. Description of Protocols

3.3.1. From PCU to PLC

3.3.2. From PLC to PCU

3.4. Data Format

Updates

Version 2.1 - Aug 97

| page | paragraph | subject | modification |
| --- | --- | --- | --- |
| 5 | 2.2.1 | transfer to CP581 | sequence of I/O bytes corrected |
| 9 | 2.4 | general command byte | siren off bit added |
| 9 | 2.4 | general status byte | "collsion switch" bit changed to "siren off" |
| 11 | 2.4 | AUX mode byte | brake interlock override bit added |
| 14 | 2.4 | equipment status byte | pendulum alarm / collison switch bit added; SAFE bit added |
| 19 | 3.4 | PCU LED status byte | PCU inactive bit added |

Version 2.2 - Sept 97

| page | paragraph | subject | modification |
| --- | --- | --- | --- |
| 4 | 2.2.1 | transfer to CP581 | DD88 thru 92: position setpoints added |
| 9 | 2.4 | general command byte | siren on/off toggle bit |
| 10 | 2.4 | mode byte | "stop executed“ bit added; bit 15 used by 581 |
| 14 | 2.4 | equipment status byte | SAFE changed to "local axis disable“ |

Version 2.3 - Dec 99

| page | paragraph | subject | modification |
| --- | --- | --- | --- |
| 11 | 2.4 | AUX & Regen status | regeneration board status added |

# 1.	General Information

## 1.1.	Foreword

This decription covers the internal interfaces between the different processors of the subreflector drive control system.

## 1.2.	Interface List

designation of interface	interface type at PLC

─────────────────────────────────────────────────────────────────

CPU 928 - CP 581	S5 bus

connection to PCU	CP 524 (TTY)

CP 581 - OCU	COM *

# 2.	Interface CPU 928  -  CP 581

## 2.1.	Transfer Requirements

Data are continuously exchanged via DP RAM. The data to be sent by each partner are refreshed during each cycle of the software.

## 2.2.	Description of Protocols

### 2.2.1.	From CPU to CP 581

Data Exchange Sequence:

- CPU 928 continuously sends new data to the DP RAM ("SEND ALL")

- CP 581 reads these data when required by its own software sequence.

Data:

Address 
(CPU 928)	meaning	unit	type/format
─────────────────────────────────────────────────────────────────

DB 221, DD 1	time	ms of day	DD/KF

DB 221, DD 3	time offset	ms	DD/KF

DB 221, DW 5	program track stack pointer	data set #	KF

DB 221, DW 6	general status drive cabinet		KM

DB 221, DW 10	mode Az		KM

DB 221, DW 11	AUX mode Az		KM

DB 221, DW 12	general status Az		KM

DB 221, DW 13	amplifier status Az		KM

DB 221, DW 14	motor status Az		KM

DB 221, DW 15	equipment status Az		KM

DB 221, DW 16	mode GD		KM

DB 221, DW 17	AUX mode GD		KM

DB 221, DW 18	general status GD		KM

DB 221, DW 19	amplifier status GD		KM

Address 
(CPU 928)	meaning	unit	type/format
─────────────────────────────────────────────────────────────────

DB 221, DW 20	motor status GD		KM

DB 221, DW 21	equipment status GD		KM

DB 221, DW 22	mode CH		KM

DB 221, DW 23	AUX mode CH		KM

DB 221, DW 24	general status CH		KM

DB 221, DW 25	amplifier status CH		KM

DB 221, DW 26	motor status CH		KM

DB 221, DW 27	equipment status CH		KM

DB 221, DW 30	measured rate Az	10-4 degr/s	KF

DB 221, DW 31	measured rate GD	10-4 degr/s	KF

DB 221, DW 32	measured rate CH	10-4 degr/s	KF

DB 221, DW 40	measured torque motor Az 11	2,852 * 10-2 lbft	KF

DB 221, DW 41	measured torque motor Az 12	2,852 * 10-2 lbft	KF

DB 221, DW 42	measured torque motor Az 51	2,852 * 10-2 lbft	KF

DB 221, DW 43	measured torque motor Az 52	2,852 * 10-2 lbft	KF

DB 221, DW 44	measured torque motor Az 41	2,852 * 10-2 lbft	KF

DB 221, DW 45	measured torque motor Az 42	2,852 * 10-2 lbft	KF

DB 221, DW 46	measured torque motor Az 81	2,852 * 10-2 lbft	KF

DB 221, DW 47	measured torque motor Az 82	2,852 * 10-2 lbft	KF

DB 221, DW 48	measured torque motor GD 11	4,031 * 10-2 lbft	KF

DB 221, DW 49	measured torque motor GD 12	4,031 * 10-2 lbft	KF

DB 221, DW 50	measured torque motor GD 21	4,031 * 10-2 lbft	KF

DB 221, DW 51	measured torque motor GD 22	4,031 * 10-2 lbft	KF

DB 221, DW 52	measured torque motor GD 31	4,031 * 10-2 lbft	KF

DB 221, DW 53	measured torque motor GD 32	4,031 * 10-2 lbft	KF

Address 
(CPU 928)	meaning	unit	type/format
─────────────────────────────────────────────────────────────────

DB 221, DW 54	measured torque motor GD 41	4,031 * 10-2 lbft	KF

DB 221, DW 55	measured torque motor GD 42	4,031 * 10-2 lbft	KF

DB 221, DW 56	measured torque motor CH 1	4,031 * 10-2 lbft	KF

DB 221, DW 57	measured torque motor CH 2	4,031 * 10-2 lbft	KF

DB 221, DD 60	measured position Az	10-4 degr	DD/KF

DB 221, DD 62	measured position GD	10-4 degr	DD/KF

DB 221, DD 64	measured position CH	10-4 degr	DD/KF

DB 221, DD 66	position encoder Az 1	counts 	DD/KF

DB 221, DD 68	position encoder Az 2	counts 1	DD/KF

DB 221, DD 70	position offset Az	10-4 degr	DD/KF

DB 221, DD 72	position offset GD	10-4 degr	DD/KF

DB 221, DD 74	position offset CH	10-4 degr	DD/KF

DB 221, DD 76	softlimit Az cw	10-4 degr	DD/KF

DB 221, DD 78	softlimit Az ccw	10-4 degr	DD/KF

DB 221, DD 80	softlimit GD up	10-4 degr	DD/KF

DB 221, DD 82	softlimit GD down	10-4 degr	DD/KF

DB 221, DD 84	softlimit CH up	10-4 degr	DD/KF

DB 221, DD 86	softlimit CH down	10-4 degr	DD/KF

DB 221, DD 88	position setpoint Az	10-4 degr	DD/KF

DB 221, DD 90	position setpoint GD	10-4 degr	DD/KF

DB 221, DD 92	position setpoint CH	10-4 degr	DD/KF

DB 221, DD 98	time since reset	sec	DD/KF

DB 221, DW 100	input status bytes 0, 1		KM

DB 221, DW 101	input status bytes 2, 3		KM

DB 221, DW 102	input status bytes 4, 5		KM

DB 221, DW 103	input status bytes 6, 7		KM

Address 
(CPU 928)	meaning	unit	type/format
─────────────────────────────────────────────────────────────────

DB 221, DW 104	input status bytes 8, 9		KM

DB 221, DW 105	input status bytes 10, 11		KM

DB 221, DW 106	input status bytes 12, 13		KM

DB 221, DW 107	input status bytes 14, 15		KM

DB 221, DW 108	input status bytes 16, 17		KM

DB 221, DW 109	input status bytes 18, 19		KM

DB 221, DW 110	output status bytes 0, 1		KM

DB 221, DW 111	output status bytes 2, 3		KM

DB 221, DW 112	output status bytes 4, 5		KM

DB 221, DW 113	output status bytes 6, 7		KM

DB 221, DW 114	output status bytes 8, 9		KM

DB 221, DW 115	output status bytes 10, 11		KM

DB 221, DW 116	output status bytes 12, 13		KM

DB 221, DW 117	output status bytes 14, 15		KM

DB 221, DW 118	output status bytes 16, 17		KM

DB 221, DW 119	output status bytes 18, 19		KM

DB 221, DW 120	spare		KM

DB 221, DW 121	spare		KM

DB 221, DW 122	status analog output 240 		KF

DB 221, DW 123	status analog output 242		KF

DB 221, DW 124	status analog output 244		KF

DB 221, DW 125	status analog output 246		KF

DB 221, DW 126	status analog output 248		KF

DB 221, DW 127	status analog output 250		KF

DB 221, DW 128	status analog output 252		KF

DB 221, DW 129	status analog output 254		KF

### 2.2.2.	From CP 581 to CPU

Data Exchange Sequence:

- CP 581 continuously sends new data to the DP RAM

- CPU reads these data if required by its own software sequence (RECEIVE ALL).

Data:

a) General Data

Address	meaning	unit	type/format
(CPU 928)	
─────────────────────────────────────────────────────────────────

DB 222, DD 1	time	ms of day	KF/DD

DB 222, DW 3	watchdog 		KF

DB 222, DW 5	clear program stack 		KF

DB 222, DW 6	general commands		KM

DB 222, DD 7	time offset	ms	DD/KF

DB 222, DW 10	selected mode Az		KM

DB 222, DW 11	AUX mode Az		KM

DB 222, DW 12	selected mode GD		KM

DB 222, DW 13	AUX mode GD		KM

DB 222, DW 14	selected mode CH		KM

DB 222, DW 15	AUX mode CH		KM

DB 222, DW 20	commanded rate Az	10-4 °/s	KF

DB 222, DW 21	commanded rate GD	10-4 °/s	KF

DB 222, DW 22	commanded rate CH	10-4 °/s	KF

DB 222, DD 24	commanded position Az	10-4 degr	KF/DD

DB 222, DD 26	commanded position GD	10-4 degr	KF/DD

DB 222, DD 28	commanded position CH	10-4 degr	KF/DD

DB 222, DD 30	position offset Az	10-4 degr	KF/DD

DB 222, DD 32	position offset GD	10-4 degr	KF/DD

DB 222, DD 34	position offset CH	10-4 degr	KF/DD

b) Program Track Data

Address	meaning	unit	type/format
(CPU 928)	
─────────────────────────────────────────────────────────────────

DB 223, DD 0	data set 1: time	ms of day	KF/DD

DB 223, DD 2	data set 1: commanded position Az	10-4 degr	KF/DD

DB 223, DD 4	data set 1: commanded position GD	10-4 degr	KF/DD

DB 223, DD 6	data set 1: commanded position CH	10-4 degr	KF/DD

.
.
.
DB 223, DD (n*8)	data set n: time	ms of day	KF/DD

DB 223, DD (n*8 + 2)	data set n: commanded position Az	10-4 degr	KF/DD

DB 223, DD (n*8 + 4)	data set n: commanded position GD	10-4 degr	KF/DD

DB 223, DD (n*8 + 6)	data set n: commanded position CH	10-4 degr	KF/DD

.
.
.

DB 223, DD 1024	data set 128: time	ms of day	KF/DD

DB 223, DD 1026	data set 128: commanded position Az	10-4 degr	KF/DD

DB 223, DD 1028	data set 128: commanded position GD	10-4 degr	KF/DD

DB 223, DD 1030	data set 128: commanded position CH	10-4 degr	KF/DD

## 2.3.	Data Formats

Data are stored in the DPRAM as words (16 bits = 2 bytes). A double precision value consists of two words. The high-word is the one with the lower address.

Format DD/KF	32 bit integer value
	MSB = sign
	negative values : two's complement

Format KF	16 bit integer value
	MSB = sign
	negative values : two's complement

Format KY	2 individual bytes
	each byte contains a positive integer value
	(range 0...255)

Format KM	16 bit word
	each bit contains its individual logical information

## 2.4.	Format of Individual Bytes

Data are stored in the DPRAM as words (16 bits = 2 bytes). A double precision value consits of two words. The high-word is the one with the lower address.

General Commands

Bits 8...15: always zero


                    ┌───────────────────────────────────────┐
                    │ 07   06   05   04   03   02   01   00 │
                    └───────────────────────────────────────┘
                       0    0              │    │    │    │    
                                           │    │    │    │   
                                           V    V    V    V
Spare 	                    1 
Siren on/off toggle bit 	                         1
Failure reset	                              1
Power on 	                                   1

General Status

┌───────────────────────────────────────┐
                    │ 15   14   13   12   11   10   09   08 │
                    └───────────────────────────────────────┘
                       │    │    │    │    │    │    │    │
                       │    │    │    │    │    │    │    │
                       V    V    V    V    V    V    V    V
cabinet doors open	1
drive power off	     1
PLC power supply fault	          1
brake power supply fault	               1
24 V power supply fault	                    1 
Drive cabinet 3 overtemp.	                         1 
Drive cabinet 2 overtemp.	                              1
Drive cabinet 1 overtemp.	                                   1


                    ┌───────────────────────────────────────┐
                    │ 07   06   05   04   03   02   01   00 │
                    └───────────────────────────────────────┘
                       │    0    │    │    │    │    │    │    
                       │         │    │    │    │    │    │   
                       V         V    V    V    V    V    V
mains over-/undervoltage	1 
bending limit	          1 
CP581 communication fault	               1 
PCU communication fault	                    1
limit override active		1
siren off	                              1
emergency off	                                   1

Mode  (command & monitoring)

┌───────────────────────────────────────┐
                    │ 15   14   13   12   11   10   09   08 │
                    └───────────────────────────────────────┘
                       X    │    │    │    │    │    │    │
                            │    │    │    │    │    │    │
                            V    V    V    V    V    V    V

local only 	     1
PCU not active 2	          1
stop executed	               1
MSC	                    1
OCU	                         1
LCU	                              1
maintenance/PCU	                                   1


                    ┌───────────────────────────────────────┐
                    │ 07   06   05   04   03   02   01   00 │
                    └───────────────────────────────────────┘
                      │    │    │    0    │    │    │    │
                      │    │    │         │    │    │    │
                      V    V    V         V    V    V    V
read new pos. offset	1
encoder preset3	     1
axis reset3	          1
Program Track	                     1
Stow	                           1
Preset	                                1
Rate	                                     1

Notes:

-	All mode bits zero --> STOP mode.

-	Only one mode may be requested at a time.

-	X: bit used by CP581; do not use from PLC

AUX and Regeneration Command & Monitoring)

┌───────────────────────────────────────┐
                    │ 15   14   13   12   11   10   09   08 │
                    └───────────────────────────────────────┘
                       │    │    │    │    │    │    │    │
                       │    │    │    │    │    │    │    │
                       V    V    V    V    V    V    V    V
regeneration board 6 failure	1
regeneration board 5 failure	     1
regeneration board 4 failure	          1
regeneration board 3 failure	               1
regeneration board 2 failure	                    1 
regeneration board 1 failure	                          1 
regeneration system warning 	                              1
brake interlock override for AUX	                                   1

                    ┌───────────────────────────────────────┐
                    │ 07   06   05   04   03   02   01   00 │
                    └───────────────────────────────────────┘
                       │    │    │    │    │    │    │    │
                       │    │    │    │    │    │    │    │
                       V    V    V    V    V    V    V    V
motor 8	1
motor 7	     1
motor 6	          1
motor 5	               1
motor 4	                    1 
motor 3	                          1 
motor/group 2	                              1
motor/group 1	                                   1
 
Notes:

-	A set bit selects the motor/motor group to be switched off.

-	Only one bit may be set at a time.

-	Bits 2...7 apply for GD only.

Axis Status

┌───────────────────────────────────────┐
                    │ 15   14   13   12   11   10   09   08 │
                    └───────────────────────────────────────┘
                       │    │    │    │    │    │    │    │
                       │    │    │    │    │    │    │    │
                       V    V    V    V    V    V    V    V
brake released	1
cable car interlock active	     1
emergency limit	          1
pos. limit	               1
pos. pre-limit	                    1
operating range	                         1
neg. pre-limit	                              1
neg. limit	                                   1


                    ┌───────────────────────────────────────┐
                    │ 07   06   05   04   03   02   01   00 │
                    └───────────────────────────────────────┘
                       │    │    │    │    │    │    │    │
                       │    │    │    │    │    │    │    │
                       V    V    V    V    V    V    V    V
brake failure	1
encoder failure	     1
motor overtemp.	          1
runaway	               1
drive enable  	                    1
failure encoder 2 	                         1
failure encoder 14	                              1
servo failure	                                   1

Amplifier Status

┌───────────────────────────────────────┐
                    │ 15   14   13   12   11   10   09   08 │
                    └───────────────────────────────────────┘
                       │    │    │    │    │    │    │    │
                       │    │    │    │    │    │    │    │
                       V    V    V    V    V    V    V    V
Ampl. 82 not ready	1
Ampl. 82 fault	     1
Ampl. 81 not ready	          1
Ampl. 81 fault	               1
Ampl. 42 not ready	                    1 
Ampl. 42 fault	                          1 
Ampl. 41 not ready	                              1
Ampl. 41 fault	                                   1


                    ┌───────────────────────────────────────┐
                    │ 07   06   05   04   03   02   01   00 │
                    └───────────────────────────────────────┘
                       │    │    │    │    │    │    │    │
                       │    │    │    │    │    │    │    │
                       V    V    V    V    V    V    V    V
Ampl. 52 not ready	1
Ampl. 52 fault	     1
Ampl. 51 not ready	          1
Ampl. 51 fault	               1
Ampl. 12 not ready	                    1 
Ampl. 12 fault	                          1 
Ampl. 11 not ready	                              1
Ampl. 11 fault	                                   1

Motor Status

Bits 8...15: always zero


                    ┌───────────────────────────────────────┐
                    │ 07   06   05   04   03   02   01   00 │
                    └───────────────────────────────────────┘
                       │    │    │    │    │    │    │    │
                       │    │    │    │    │    │    │    │
                       V    V    V    V    V    V    V    V
motor 82 overtemp.	1
motor 81 overtemp	     1
motor 42 overtemp	          1
motor 41 overtemp	               1
motor 52 overtemp	                    1 
motor 51 overtemp	                          1 
motor 12 overtemp	                              1
motor 11 overtemp	                                   1

Equipment Status

┌───────────────────────────────────────┐
                    │ 15   14   13   12   11   10   09   08 │
                    └───────────────────────────────────────┘
	│    0    0    │    0    0    0    0
	│              │                    
	V              V                    
Pendulum alarm 
   / collision switch 	1                                  
local axis disable	               1                    

                    ┌───────────────────────────────────────┐
                    │ 07   06   05   04   03   02   01   00 │
                    └───────────────────────────────────────┘
                       │    │    │    │    │    │    │    │
                       │    │    │    │    │    │    │    │
                       V    V    V    V    V    V    V    V
fault brakes group 2	1
fault brakes group 1 	     1
DC bus 2 fault	          1
DC bus 1 fault	               1
main contactor 2 on	                    1 
main contactor 1 on 	                          1 
power supply 2 fault	                              1
power supply 1 fault	                                   1

Rate

Integer values for commanded velocity

Max. values:	Az	±4170 * 10-4 °/s =  25 °/min
	GD, CH	±417 * 10-4 °/s   =  2.5 °/min

Position

Integer values for commanded/actual position

Max. values:	Az	±3,600,000 * 10-4 ° =  ± 360 °
	GD, CH	0 ... 200,000 * 10-4 °   =  0 ... 20 °

Clear Stack Command

integer "1"	clear stack
any other value	no activity

Watchdog

always integer "20"

Input / Output Status Bytes n, n+1

┌───────────────────────────────────────┐
                    │ 15   14   13   12   11   10   09   08 │
                    └───────────────────────────────────────┘
                       │    │    │    │    │    │    │    │
                       │    │    │    │    │    │    │    │
                       V    V    V    V    V    V    V    V

Byte n      bits	7    6    5    4    3    2    1    0


                    ┌───────────────────────────────────────┐
                    │ 07   06   05   04   03   02   01   00 │
                    └───────────────────────────────────────┘
                       │    │    │    │    │    │    │    │
                       │    │    │    │    │    │    │    │
                       V    V    V    V    V    V    V    V

Byte n+1    bits	7    6    5    4    3    2    1    0

# 3.	Interface to PCU

## 3.1.	Hardware

at PLC:	CP 524
at PCU:	Becker UCU
interface type	TTY 20 mA

## 3.2.	Transfer Requirements

transfer speed:	9600 Bd
no. of data bits:	8
no of stop bits 	1 
parity	none

transfer PCU --> PLC	every 100 ms (if PCU is plugged in)
transfer PLC --> PCU	once after each transmission by PCU

## 3.3.	Description of Protocols

### 3.3.1.	From PCU to PLC

Only one type of protocol is sent.

Word-No.                                       Contents hex.
        ┌──────────────────────────────────┐
1       │         start word               │   AA55
        │==================================│
2       │       mode selection             │
        │==================================│
3       │       function selection         │
        │==================================│
4       │       rate potentiometer         │
        │==================================│
5       │          Checksum                │
        │==================================│
6       │          end word                │   0303
        └──────────────────────────────────┘

### 3.3.2.	From PLC to PCU

Only one type of protocol is sent.

Word-No.                                       Contents hex.
        ┌──────────────────────────────────┐
1       │         start word               │   BB66
        │==================================│
2       │         LED status               │
        │==================================│
3       │         actual current           │
        │==================================│
4       │       actual position I          │
        │==================================│
5       │       actual position II         │
        │==================================│
6       │          checksum                │
        │==================================│
7       │          end word                │   0303
        └──────────────────────────────────┘

## 3.4.	Data Format

Data transfer is done word by word; one word contains 2 bytes, i.e. 16 bit. The high-byte is always sent first.

The MSB ist set in all data words.

Start word	e.g. AA55, see a.m. protocol definition

End word	0303H

Checksum	sum of all data words 
	(incl. start word, without end word)

The individual words - disregarding their meaning - will be added as 16 bit integer values with the MSB representing the sign (1=negative). Negative values will be considered as two's complement numbers.

The lower 16 bits of the sum of all data will be transferred as "checksum". Bit 15 and 07 - i.e. the MSBs of both bytes - will always be set; i.e. the checksum will be masked with 8080H.

Mode Selection

┌───────────────────────────────────────┐
                    │ 15   14   13   12   11   10   09   08 │
                    └───────────────────────────────────────┘
                       1    │    0    0    0    0    0    0
                            │                              
                            │                              
                            V                             
Emergency off	     1


                    ┌───────────────────────────────────────┐
                    │ 07   06   05   04   03   02   01   00 │
                    └───────────────────────────────────────┘
                       0    0    0    0    0    │    │    │
                                                │    │    │
                                                │    │    │
                                                V    V    V

Carriage House	                         1
Greg. Dome	                              1
Azimuth	                                   1

Note:

Only one bit in the mode selection word may be set.

Function Selection

Bit 15: "1"
Bit 8-14: "0"

┌───────────────────────────────────────┐
                        │ 07   06   05   04   03   02   01   00 │
                        └───────────────────────────────────────┘
                           │    0    │    │    0    0    │    │
                           V         │    │              │    │
reset	1         V    V              │    │
move command "ready" 	          1    0              │    │
move command "go"	          0    1              V    V
drive off	                              1    0
drive on 	                              0    1

LED Status

┌───────────────────────────────────────┐
               │ 15   14   13   12   11   10   09   08 │
               └───────────────────────────────────────┘
                  1    │    │    │    0    0    │    │
                       │    │    │              │    │
                       │    │    │              │    │
                       V    V    V              V    V
PCU inactive 	     1
ready	          1
go	               1
drive off		               1     
drive on 		                    1

               ┌───────────────────────────────────────┐
               │ 07   06   05   04   03   02   01   00 │
               └───────────────────────────────────────┘
                                 │    │    │    │    │
                                 │    │    │    │    │
                                 │    │    │    │    │
                                 V    V    V    V    V
prelimit up/cw		1
prelimit down/ccw		     1
limit up/cw		          1
limit down/ccw		               1
servo failure		                    1

Current,	bits 0...13: 	14 bit integer value
Rate Potentiometer		as multiple of 0.1 %

	bit 14:sign (1=negative)
	Bit 15 (MSB):	always 1

	data range:	0...100.0%

Position	

Word I	14 bit integer value
	as multiple of 1.000°

	bit 0...13: 	data bits
	bit 14: 	sign (1=negative)
	bit 15 (MSB):	always "1"

Word II	14 bit integer value
	as multiple of 0.0001°

	bit 0...13: 	data bits
	bit 15 (MSB):	always "1"

# Footnotes

one encoder count in Az = 1.441775 * 10-4 degr

from CPU928 to CP581 only

from CP581 to CPU928 only

Az only

Az: pendulum alarm, GD/CH: collision switch encountered

24V LED flashing