ARECIBO OBSERVATORY
SERVO DRIVE SYSTEM UPGRADE
Volume IV
MAINTENANCE MANUAL
CONTROL SYSTEMS
Vendor Publications
File 1
Provided for
National Astronomy and Ionosphere Center
Cornell University
Ithaca, NY, USA
Project No. 10/95034
Rev.: 2.2
September 1997

Vertex Antennentechnik GmbH Baumstr. 50 47198 Duisburg Germany Tel. +49-2066-2096-0; Fax -11	Vertex Communications Corporation 2600 Longview Street Kilgore, TX 75663 U.S.A. Tel. 903-984-0555; Fax -1826

Contents
Note:
Manufacturer's documentation marked with * below is supplied as a separate manual.

1.	Programmable Controller Siemens Simatic S5-135U
1.1	Manual Programmable Controller S5-135U/155U	*
1.2	Manual CPU 928B	*
1.3	Manual CP 581	*
1.4	Manual CP 524 / COM 525	*
1.5	Position Measuring Module WF 705
1.6	LAN Interface Module
1.7	Time Code Reader
2.	Brushless Drive System
2.1	Data Sheets Kollmorgen Motors B-604 / B-606
2.2	Manual Amplifier BDS 4A	*
2.3	Technical Data Maccon Regeneration Module
3.	Optical Encoder System
3.1	Encoders
3.2	Encoder Interface Modules
4.	Vertex Portable Control Unit
5.	Limit Switches
5.1	Stromag Rotary Cam Switches
5.2	Schmersal Limit Switches
6.	Vertex Drive Control System
6.1	Azimuth / Grgorian Dome
6.2	Carriage House
7.	Uninterruptable Power Supply
8.	Switchgear Inside Drive Cabinet
8.1	Dold Voltage Supervision Relays
8.2	Pilz Current Relays
8.3	Schiele Overvoltage Protection Relay
8.4	Miscelleanous Components

For addresses of manufacturers see following pages.
Addresses Of Manufacturers

No.	Unit	Manufacturer	US Office
1.1 1.2 1.3 1.4	Programmable Logic Controller (PLC)	Siemens AG Bereich Industrie- Automatisierungssysteme Postfach 4848 D-90327 Nürnberg Phone +49-911-654-0 Fax +49-911-654-4064	Siemens Industrial Automation Inc. 100 Technology Drive Alpharetta, GA 30202 Phone 404-740-3090 Fax 404-740-3798
1.5	LAN Interface Module	3Com Corporation 5400 Bayfront Plaza Santa Clara, CA 95052-8145 Phone 800-NET-3COM or 408-764-5000	<---
1.6	Time Code Reader	Bancomm Division of Datum Inc. 6541 Via del Oro San Jose, CA 95119 Phone 408-578-4161 Fax 408-758-4165	<---
2.1 2.2	Kollmorgen Motors & Amplifiers	Industrial Drives 201 Rock Road Radford, VA 24141 Phone 540-639-2495 Fax 540-731-0847	<---
2.3	Regeneration Modules	Maccon GmbH Kühbachstr. 9 D-81543 München Phone +49-89-66 20 62 Fax +49-89-65 52 17
3.1 3.2	Optical Encoder System	TR Electronic GmbH Eglishalde 6 D-78647 Trossingen Phone +49-7425-228-0 Fax +49-7425-228-33	TR Encoder Solutions Inc P.O. Box 4448 Troy, MI 48099 Phone 800-709-3300 Fax 810-244-8741
4	Portable Control Unit	VERTEX

No.	Unit	Manufacturer	US Office
5.1	Cam Limit Switches	Maschinenfabrik Stromag GmbH Hansastr. 120 D-59425 Unna Phone +49-2303-102-0 Fax +49-2203-102-201	Stromag, Inc. 85 Westpark Road P.O. Box 250 Centerville (Dayton), OH 45459 Phone 513-433-3882 Fax 513-433-6598
5.2	Mech. Limit Switches	Schmersal GmbH & Co. Möddinghofe 30 D-42279 Wuppertal Phone +49-202-201-0 Fax +49-202-201-100	E & E Controls, Inc. 5 West Cross St. Hawthorne, NY 10532 Phone 914-769-5000 Fax 914-769-3641
6.	Drive Control System	VERTEX
7.	Uninterruptable Power Supply	American Power Conversion Corp. 132 Fairgrounds Park P.O. Box 278 West Kingston, RI 02892 Phone 800-800-4272 Fax 401-789-3710	<---
8.1	Voltage Supervision Relays	E. Dold & Söhne KG - Relaisfabrik Postfach 60 D-78114 Furtwagen Phone +49-7723-6540 Fax +49-7723-654356	Altech Corporation Mr. Friedrich 35 Royal Road Flemington NJ 08822-6000 Phone 908-806-9400 Fax 908-806-9490
8.2.	Current Relays	pilz GmbH & Co. Postfach 725 D-73708 Esslingen Phone +49-711-3409-0 Fax +49-711-3409-133	pilz Inc. 24850 Drake Road Farmington Hills US Michigan 48335 Phone 810-473-1133 Fax 810-473-3997
8.3.	Overvoltage Protection Relay	Schiele Industriewerke GmbH Postfach 120 D-78127 Hornberg Phone +49-7833-78-0 Fax +49-7833-78-318	Entrelec Inc. 1950 Hurd Drive Irving, TX 75038-4312 Phone 214-550-9025 Fax 214-550-9215

Vertex Addresses:
Vertex Antennentechnik GmbH
Baumstr. 50
D-47198 Duisburg
Phone +49-2066-2096-0
Fax +49-2066-2096-11
Vertex Communications Corp.
2600 Longview Str.
Kilgore, TX 75663
Phone 903-084-0555
Fax 903-984-1826
2. Kollmorgen Motors
Motor Replacement

Before removing of a motor the two connectors at the motor have to be loosened. If a spare motor is not installed immediately afterwards, the following instructions have to be observed:
-	Unplug resolver connector (C2) at the related amplifier in the drive cabinet.
Otherwise the resolver supply voltage might be shorted at the pins of the motor connector. This in return could destroy the amplifier itself.
-	Protect motor connectors against ingress of water (by cover, ahnging upside down etc.).

Internal Brakes
Manufacturer / Part Number
Manufacturer:	Stromag, Inc.
85 Westpark Rd.
Centerville (Dayton), OH 45459
Phone: (937) 433.3882
Fax. (937) 433 6598
Part Number of Friction Disc S/A::	10-01125-02

Minimum Friction Disc Thickness
The minimum thicckness is 0.230 in.

Brake check / replacement
The friction disc dimensions can only be measured when the brake housing is removed from the motor. To do this, remove the cover plate from the rear end of the motor. Please note that there is an O-ring directly under the plate, and care should be taken so as not to damage the O-ring during disassembly / re-assembly of the motor.
For measuring the friction disc thickness the brake housing (extension of the motor housing) also has to be removed (screws "A" on attached drawing).
If the brake itself has to be removed, proceed as follows: The brake is held in place with 3 bolts. Remove these, and then slide the brake off the motor shaft. There should be enough lead length so that the brake can be removed from the motor without having to remove the lead wires from the connector. The splined hub will remain attached to the shaft; this does not have to be removed for inspection. Once the brake is outside the motor body, the brake windings must be energized to measure the air gap. The brake will open with power on.
Brake Drawing
Note:
The lower half (with extended length) of the drawing depicts an option with a brush tachometer. The Arecibo motors do not have this option. Therefore only the inner section (the brake itself) of the lower half of the drawing is applicable.
6.	VERTEX DRIVE CONTROL SYSTEM
VERTEX Drive Control System
1. Introduction
The Vertex Drive Control System has been designed for the use in the Arecibo Servo Drive System. It is, however, based on standard components that Vertex frequently uses for high precision drives which require special measures in order to reach the specified accuracies. Such measures are
-	anti-backlash compensation
-	differential velocity control
-	combination of torque setpoint out of different contributing factors.
The Vertex Drive Control System consists of several analog printed circuit boards; thus it can be used with many different types of controllers.
2. Overview
The Drive Control System (DCS) performs all drive control tasks which are particularly caused by the motor arrangement at Arecibo Observatory, such as
-	torque biassing
-	torque equalization
-	gravity compensation.
In addition to that the DCS provides a possibility to operate the drives at a very low level. Each axis can be operated separately in jog mode by forward/reverse pushbuttons. The speed can be selected by a potentiometer.
The DCS is a separate 19" 4HU rack mounted unit for each axis. It comprises
-	power supply
-	analog printed circuit boards for
. acceleration limiter
. differential velocity control
. velocity loop
. torque bias.
-	pushbuttons and potentiometers for low level operation.
The figures on pages 5 and 6 show the arrangement of the velocity and torque control loops. The principle design is similar for Azimuth and Gregorian Dome. Only settings of the individual boards, the way of connecting the individual motors to the DCS and the modes (activated by the PLC) are different. The Carriage House DCS also is kept as similar as possible to Az and GD. However, it comprises only a few boards.
3. Control Concept for 1 Axis
Each axis has one (1) velocity control loop. The velocity setpoint is received from the PLC (position loop output), the actual velocity is the average velocity of the eight (8) motors of the resp. axis (CH#1: two motors).
This PLC velocity setpoint - though having passed a software velocity and acceleration limiter inside the PLC - is run through a hardware acceleration limiter.
For GD and CH axes a gravity compensation is activated. Since the major part of the required torque is caused by gravity, a calculated current setpoint is feedforwarded by the PLC directly to the current setpoint output of the DCS. Thus, the velocity controller has to deal with deviations only and is able to reach the desired position much faster than without feedforward.
A torque bias is added between
-	the two pairs of motors on each side of the feed arm (Az)
-	the two motors of each truck (GD, CH)
The torque bias compensates for the backlash of the gearbox, allowing smooth performance at velocities » 0. The torque bias for GD and CH depends on the actual position and is fed from the PLC. At elevation zero it reaches its maximum, at elevation 20 degr. there is no more torque bias because the drives are preloaded by gravity and work together in one torque direction only.
The resulting current setpoint is fed to all servo amplifiers, thus providing even torque distribution for all motors (disregarding corrections).
Differential velocity controller evaluation and control is provided for
-	each pair of motors
. Az: the two opposing (inner and outer) motors of one trolley
. El: the two motors of one truck
-	each pair of trolleys at one side of the feed arm (Az only)
-	the two sides of the feed arm (Az only).
A speed zero signal is derived from the actual velocity signals and fed back to the PLC.

Control Concept Azimuth
AZKONZ.SKD
Control Concept Elevation
ELKONZ.SKD
4. Arrangement Of Boards
The Vertex Drive Control System consists of four main types of boards:
-	Setpoint Selection and Acceleration Limiter (board # 295.4):
. velocity setpoint selection
. acceleration limiter (two different ramps selectable)
. velocity limitation at prelimits
-	Actual Velocity Detection (board # 329.3):
. evaluation of two tachos
. derivation of sum and differential velocities
. zero speed detection
. tacho failure detection
-	Velocity Controller (board # 334.3)
. PI velocity controller
. differential velocity controller
. torque bias generation
. combination of torque setpoint components
. output limitation
-	Universal Amplifier (board # 421.0)
. four amplifier channels with up two three selectable inputs each
 and selectable output polarity
. one signal inverter with adjustable gains.
The following auxiliary boards are used (Az and GD only):
-	Inverter Board (board # 873.0)
six signal inverters for generating the differential velocity signals with both polarities
-	Highpass Filter Board (board # 883.0)
six highpass filters for the differential velocity signals
5. Functional Description
All control signal activation as well as reactions on signals generated by the Drive Control System is performed by the PLC.
Block diagrams for the individual boards and detailed circuit diagrams for the Vertex Drive Control System boards can be found hereafter.

5.1. Acceleration Limiter Board 295.4
By relays K1...K6 one out of six velocity command signals can be selected.[1] If none is selected, the velocity command can be connected to GND by K7.
[1] Only two setpoints (from PLC and from potentiometer) are used
The velocity command is run through an acceleration limiter. With K10 not enabled a slow ramp is active, with K10 enabled a faster ramp is active.
With prelimit signals connected to the K8 and K9 inputs a limitation of the commanded velocity to 10% of the maximum value can be achieved. The limitation is active with K8 and K9 not enabled (fail safe mode).
Relay outputs K11 and K12 provide information about the command signal polarity to be used in a computer etc.[2]
[2] unused feature
Two additional relays (k13 and K14) can be used for customer purposes.[3]
[3] unused feature
Test sockets at front panel:
MP1	active velocity command	±10 V
MP2	limited velocity command (after prelimits)	±10 V
MP3	velocity command output	±10 V
LEDs at front panel:
H1	positive velocity command
H2	negative velocity command
5.2. Actual Velocity Board 329.3
The actual velocity of two tachos is evaluated. The input voltage from the tachos is scaled to ±10V. The two velocities are added and scaled again to reach ±10V for the sum (Sn/2). This sum is used as actual velocity input for the velocity controller. The two tachos can be selected individually. So in case of e.g. loss of one drive only one tacho will be used for sum speed evaluation. The output scaling for Sn/2 remains the same. No controller adjustments are required.
In addition to Sn/2 the difference Dn of the two tachos is also generated. A low-pass filter is removes higher-frequency interference outside the bandwidth of the control system. This Dn signal is also fed to the velocity controller board.
Besides this handling of the actual velocities two digital signals are derived:
-	zero speed, indicating that Sn/2 is below an adjustable threshold
-	tacho failure, indicating that Dn is above an adjustable threshold.
Test sockets at front panel:
MP1	actual velocity 1	±10 V
MP2	actual velocity 2	±10 V
MP3	differential velocity (Dn)	±10 V
MP4	sum velocity (Sn/2)	±10 V
LEDs at front panel:
H1	tacho 2 activated
H2	tacho 1activated
H3	tacho failure
H4	speed zero
5.3. Velocity Controller Board 334.3
A velocity deviation is derived using the desired speed vdes fed by the PLC and the actual velocity measured by the actual velocity board (Sn/2).
The deviation is fed to the summation speed controller. A limiter adapts the maximum value of the desired current ides to the current controller. The current setpoint is fed to two outputs simultaneously.
Constant desired current values of the same magnitude but different sign are superimposed to the two current setpoints in order to compensate for the gear backlash.[4]
[4] This feature (constant torque bias) is used for Azimuth only
A third component for the current setpoint is generated in the differential velocity controller. The differential speed Dn generated by the actual velocity board is fed to a proportional controller via a filter network. The low-pass filter (on board 329.3) is designed to remove higher-frequency interference outside the bandwidth of the control system, whereas the highpass filter (on board 334.3) ensures that only the undesirable oscillations between the two motors are covered, but not the static error of the tacho generators. The differential current setpoint is superimposed positively or negatively on the summation current desired value ides.[5]
[5] This feature (Dn function on board 334.3) is used for Carriage House #1 only
A fourth component contributing to the output current setpoint is fed directly from the PLC. It can be activated by relay K3[6].
[6] Used for gravity compensation (GD) respectively a combined gravity comp./torque bias signal (CH)
The sum current setpoints to the two motor controllers are limited to ±10V.
Test sockets at front panel:
MP1	velocity deviation (Sn/2 - Dn) * 10	±15 V
MP2	output of velocity controller	±15 V
MP3	output to motor controller 1 (ides1)	±10 V
MP4	output to motor controller 2 (ides2)	±10 V
MP5	sum current setpoint motor 1	±15 V
MP6	sum current setpoint motor 2	±15 V
LEDs at front panel:
H1	torque bias activated
H2	velocity controller activated
H3	external torque component activated
H4	differential velocity controller activated
H5	I channel activated
5.4. Universal Amplifier Board 421.0
This board includes four amplifier channels with up two three selectable inputs each and selectable output polarity.
One input is fed directly to the amplifier and is always active. The other two inputs can be enabled and disabled by relays K1...K4. The output polarity can be swapped by jumpers W *03. The overall gain is adjustable by resistors.
An additional channel can be used as inverter, sum point or filter depending on the resistors and capacitors used.
Test sockets at front panel:
MP11 / MP12	positive / negative output of amplifier 1	±10 V
MP21 / MP22	positive / negative output of amplifier 2	±10 V
MP31 / MP32	positive / negative output of amplifier 3	±10 V
MP41 / MP42	positive / negative output of amplifier 4	±10 V
MP51	output of amplifier 5	±10 V