ARECIBO OBSERVATORY
SERVO DRIVE SYSTEM UPGRADE
Volume II - Section 3
OPERATION AND MAINTENANCE MANUAL
CONTROL SYSTEMS
Programmable Controller Siemens Simatic S5-135U
DESCRIPTION OF INTERNAL INTERFACES
Provided for
National Astronomy and Ionosphere Center
Cornell University
Ithaca, NY, USA
Project No. 10/95034
Rev.: 2.3
December 1999

Vertex Antennentechnik GmbH Baumstr. 50 47198 Duisburg Germany Tel. +49-2066-2096-0; Fax -11	Vertex Communications Corporation 2600 Longview Street Kilgore, TX 75663 U.S.A. Tel. 903-984-0555; Fax -1826

Contents

Updates
Version 2.1 - Aug 97
page	paragraph	subject	modification
5	2.2.1	transfer to CP581	sequence of I/O bytes corrected
9	2.4	general command byte	siren off bit added
9	2.4	general status byte	"collsion switch" bit changed to "siren off"
11	2.4	AUX mode byte	brake interlock override bit added
14	2.4	equipment status byte	pendulum alarm / collison switch bit added; SAFE bit added
19	3.4	PCU LED status byte	PCU inactive bit added

Version 2.2 - Sept 97
page	paragraph	subject	modification
4	2.2.1	transfer to CP581	DD88 thru 92: position setpoints added
9	2.4	general command byte	siren on/off toggle bit
10	2.4	mode byte	"stop executed“ bit added; bit 15 used by 581
14	2.4	equipment status byte	SAFE changed to "local axis disable“

Version 2.3 - Dec 99
page	paragraph	subject	modification
11	2.4	AUX & Regen status	regeneration board status added

# 1. General Information
## 1.1. Foreword
This decription covers the internal interfaces between the different processors of the subreflector drive control system.

## 1.2. Interface List
designation of interface	interface type at PLC
─────────────────────────────────────────────────────────────────
CPU 928 - CP 581	S5 bus
connection to PCU	CP 524 (TTY)
CP 581 - OCU	COM *
# 2. Interface CPU 928 - CP 581
## 2.1. Transfer Requirements
Data are continuously exchanged via DP RAM. The data to be sent by each partner are refreshed during each cycle of the software.

## 2.2. Description of Protocols
### 2.2.1. From CPU to CP 581
Data Exchange Sequence:
- CPU 928 continuously sends new data to the DP RAM ("SEND ALL")
- CP 581 reads these data when required by its own software sequence.
Data:
Address
(CPU 928)	meaning	unit	type/format
─────────────────────────────────────────────────────────────────
DB 221, DD 1	time	ms of day	DD/KF
DB 221, DD 3	time offset	ms	DD/KF
DB 221, DW 5	program track stack pointer	data set #	KF
DB 221, DW 6	general status drive cabinet	KM
DB 221, DW 10	mode Az	KM
DB 221, DW 11	AUX mode Az	KM
DB 221, DW 12	general status Az	KM
DB 221, DW 13	amplifier status Az	KM
DB 221, DW 14	motor status Az	KM
DB 221, DW 15	equipment status Az	KM
DB 221, DW 16	mode GD	KM
DB 221, DW 17	AUX mode GD	KM
DB 221, DW 18	general status GD	KM
DB 221, DW 19	amplifier status GD	KM
Address
(CPU 928)	meaning	unit	type/format
─────────────────────────────────────────────────────────────────
DB 221, DW 20	motor status GD	KM
DB 221, DW 21	equipment status GD	KM
DB 221, DW 22	mode CH	KM
DB 221, DW 23	AUX mode CH	KM
DB 221, DW 24	general status CH	KM
DB 221, DW 25	amplifier status CH	KM
DB 221, DW 26	motor status CH	KM
DB 221, DW 27	equipment status CH	KM
DB 221, DW 30	measured rate Az	10-4 degr/s	KF
DB 221, DW 31	measured rate GD	10-4 degr/s	KF
DB 221, DW 32	measured rate CH	10-4 degr/s	KF
DB 221, DW 40	measured torque motor Az 11	2,852 * 10-2 lbft	KF
DB 221, DW 41	measured torque motor Az 12	2,852 * 10-2 lbft	KF
DB 221, DW 42	measured torque motor Az 51	2,852 * 10-2 lbft	KF
DB 221, DW 43	measured torque motor Az 52	2,852 * 10-2 lbft	KF
DB 221, DW 44	measured torque motor Az 41	2,852 * 10-2 lbft	KF
DB 221, DW 45	measured torque motor Az 42	2,852 * 10-2 lbft	KF
DB 221, DW 46	measured torque motor Az 81	2,852 * 10-2 lbft	KF
DB 221, DW 47	measured torque motor Az 82	2,852 * 10-2 lbft	KF
DB 221, DW 48	measured torque motor GD 11	4,031 * 10-2 lbft	KF
DB 221, DW 49	measured torque motor GD 12	4,031 * 10-2 lbft	KF
DB 221, DW 50	measured torque motor GD 21	4,031 * 10-2 lbft	KF
DB 221, DW 51	measured torque motor GD 22	4,031 * 10-2 lbft	KF
DB 221, DW 52	measured torque motor GD 31	4,031 * 10-2 lbft	KF
DB 221, DW 53	measured torque motor GD 32	4,031 * 10-2 lbft	KF
Address
(CPU 928)	meaning	unit	type/format
─────────────────────────────────────────────────────────────────
DB 221, DW 54	measured torque motor GD 41	4,031 * 10-2 lbft	KF
DB 221, DW 55	measured torque motor GD 42	4,031 * 10-2 lbft	KF
DB 221, DW 56	measured torque motor CH 1	4,031 * 10-2 lbft	KF
DB 221, DW 57	measured torque motor CH 2	4,031 * 10-2 lbft	KF
DB 221, DD 60	measured position Az	10-4 degr	DD/KF
DB 221, DD 62	measured position GD	10-4 degr	DD/KF
DB 221, DD 64	measured position CH	10-4 degr	DD/KF
DB 221, DD 66	position encoder Az 1	counts [1]	DD/KF
DB 221, DD 68	position encoder Az 2	counts 1	DD/KF
DB 221, DD 70	position offset Az	10-4 degr	DD/KF
DB 221, DD 72	position offset GD	10-4 degr	DD/KF
DB 221, DD 74	position offset CH	10-4 degr	DD/KF
DB 221, DD 76	softlimit Az cw	10-4 degr	DD/KF
DB 221, DD 78	softlimit Az ccw	10-4 degr	DD/KF
DB 221, DD 80	softlimit GD up	10-4 degr	DD/KF
DB 221, DD 82	softlimit GD down	10-4 degr	DD/KF
DB 221, DD 84	softlimit CH up	10-4 degr	DD/KF
DB 221, DD 86	softlimit CH down	10-4 degr	DD/KF
DB 221, DD 88	position setpoint Az	10-4 degr	DD/KF
DB 221, DD 90	position setpoint GD	10-4 degr	DD/KF
DB 221, DD 92	position setpoint CH	10-4 degr	DD/KF
DB 221, DD 98	time since reset	sec	DD/KF
DB 221, DW 100	input status bytes 0, 1	KM
DB 221, DW 101	input status bytes 2, 3	KM
DB 221, DW 102	input status bytes 4, 5	KM
DB 221, DW 103	input status bytes 6, 7	KM
[1] one encoder count in Az = 1.441775 * 10-4 degr
Address
(CPU 928)	meaning	unit	type/format
─────────────────────────────────────────────────────────────────
DB 221, DW 104	input status bytes 8, 9	KM
DB 221, DW 105	input status bytes 10, 11	KM
DB 221, DW 106	input status bytes 12, 13	KM
DB 221, DW 107	input status bytes 14, 15	KM
DB 221, DW 108	input status bytes 16, 17	KM
DB 221, DW 109	input status bytes 18, 19	KM
DB 221, DW 110	output status bytes 0, 1	KM
DB 221, DW 111	output status bytes 2, 3	KM
DB 221, DW 112	output status bytes 4, 5	KM
DB 221, DW 113	output status bytes 6, 7	KM
DB 221, DW 114	output status bytes 8, 9	KM
DB 221, DW 115	output status bytes 10, 11	KM
DB 221, DW 116	output status bytes 12, 13	KM
DB 221, DW 117	output status bytes 14, 15	KM
DB 221, DW 118	output status bytes 16, 17	KM
DB 221, DW 119	output status bytes 18, 19	KM
DB 221, DW 120	spare	KM
DB 221, DW 121	spare	KM
DB 221, DW 122	status analog output 240	KF
DB 221, DW 123	status analog output 242	KF
DB 221, DW 124	status analog output 244	KF
DB 221, DW 125	status analog output 246	KF
DB 221, DW 126	status analog output 248	KF
DB 221, DW 127	status analog output 250	KF
DB 221, DW 128	status analog output 252	KF
DB 221, DW 129	status analog output 254	KF
### 2.2.2. From CP 581 to CPU
Data Exchange Sequence:
- CP 581 continuously sends new data to the DP RAM
- CPU reads these data if required by its own software sequence (RECEIVE ALL).
Data:
a) General Data

Address	meaning	unit	type/format
(CPU 928)
─────────────────────────────────────────────────────────────────
DB 222, DD 1	time	ms of day	KF/DD
DB 222, DW 3	watchdog	KF
DB 222, DW 5	clear program stack	KF
DB 222, DW 6	general commands	KM
DB 222, DD 7	time offset	ms	DD/KF
DB 222, DW 10	selected mode Az	KM
DB 222, DW 11	AUX mode Az	KM
DB 222, DW 12	selected mode GD	KM
DB 222, DW 13	AUX mode GD	KM
DB 222, DW 14	selected mode CH	KM
DB 222, DW 15	AUX mode CH	KM
DB 222, DW 20	commanded rate Az	10-4 °/s	KF
DB 222, DW 21	commanded rate GD	10-4 °/s	KF
DB 222, DW 22	commanded rate CH	10-4 °/s	KF
DB 222, DD 24	commanded position Az	10-4 degr	KF/DD
DB 222, DD 26	commanded position GD	10-4 degr	KF/DD
DB 222, DD 28	commanded position CH	10-4 degr	KF/DD
DB 222, DD 30	position offset Az	10-4 degr	KF/DD
DB 222, DD 32	position offset GD	10-4 degr	KF/DD
DB 222, DD 34	position offset CH	10-4 degr	KF/DD
b) Program Track Data
Address	meaning	unit	type/format
(CPU 928)
─────────────────────────────────────────────────────────────────
DB 223, DD 0	data set 1: time	ms of day	KF/DD
DB 223, DD 2	data set 1: commanded position Az	10-4 degr	KF/DD
DB 223, DD 4	data set 1: commanded position GD	10-4 degr	KF/DD
DB 223, DD 6	data set 1: commanded position CH	10-4 degr	KF/DD
.
.
.
DB 223, DD (n*8)	data set n: time	ms of day	KF/DD
DB 223, DD (n*8 + 2)	data set n: commanded position Az	10-4 degr	KF/DD
DB 223, DD (n*8 + 4)	data set n: commanded position GD	10-4 degr	KF/DD
DB 223, DD (n*8 + 6)	data set n: commanded position CH	10-4 degr	KF/DD
.
.
.
DB 223, DD 1024	data set 128: time	ms of day	KF/DD
DB 223, DD 1026	data set 128: commanded position Az	10-4 degr	KF/DD
DB 223, DD 1028	data set 128: commanded position GD	10-4 degr	KF/DD
DB 223, DD 1030	data set 128: commanded position CH	10-4 degr	KF/DD
## 2.3. Data Formats
Data are stored in the DPRAM as words (16 bits = 2 bytes). A double precision value consists of two words. The high-word is the one with the lower address.
Format DD/KF	32 bit integer value
MSB = sign
negative values : two's complement
Format KF	16 bit integer value
MSB = sign
negative values : two's complement
Format KY	2 individual bytes
each byte contains a positive integer value
(range 0...255)
Format KM	16 bit word
each bit contains its individual logical information

## 2.4. Format of Individual Bytes
Data are stored in the DPRAM as words (16 bits = 2 bytes). A double precision value consits of two words. The high-word is the one with the lower address.
General Commands
Bits 8...15: always zero
        ┌───────────────────────────────────────┐
        │ 07 06 05 04 03 02 01 00 │
        └───────────────────────────────────────┘
        0 0 │ │ │ │
        │ │ │ │
        V V V V
Spare	1
Siren on/off toggle bit	1
Failure reset	1
Power on	1
General Status
        ┌───────────────────────────────────────┐
        │ 15 14 13 12 11 10 09 08 │
        └───────────────────────────────────────┘
        │ │ │ │ │ │ │ │
        │ │ │ │ │ │ │ │
        V V V V V V V V
cabinet doors open	1
drive power off	1
PLC power supply fault	1
brake power supply fault	1
24 V power supply fault	1
Drive cabinet 3 overtemp.	1
Drive cabinet 2 overtemp.	1
Drive cabinet 1 overtemp.	1
        ┌───────────────────────────────────────┐
        │ 07 06 05 04 03 02 01 00 │
        └───────────────────────────────────────┘
        │ 0 │ │ │ │ │ │
        │ │ │ │ │ │ │
        V V V V V V V
mains over-/undervoltage	1
bending limit	1
CP581 communication fault	1
PCU communication fault	1
limit override active	1
siren off	1
emergency off	1
Mode (command & monitoring)
        ┌───────────────────────────────────────┐
        │ 15 14 13 12 11 10 09 08 │
        └───────────────────────────────────────┘
        X │ │ │ │ │ │ │
        │ │ │ │ │ │ │
        V V V V V V V
local only [2]	1
PCU not active 2	1
stop executed	1
MSC	1
OCU	1
LCU	1
maintenance/PCU	1
        ┌───────────────────────────────────────┐
        │ 07 06 05 04 03 02 01 00 │
        └───────────────────────────────────────┘
        │ │ │ 0 │ │ │ │
        │ │ │ │ │ │ │
        V V V V V V V
read new pos. offset[3]	1
encoder preset3	1
axis reset3	1
Program Track	1
Stow	1
Preset	1
Rate	1
[2] from CPU928 to CP581 only
[3] from CP581 to CPU928 only
Notes:
-	All mode bits zero --> STOP mode.
-	Only one mode may be requested at a time.
-	X: bit used by CP581; do not use from PLC
AUX and Regeneration Command & Monitoring)

        ┌───────────────────────────────────────┐
        │ 15 14 13 12 11 10 09 08 │
        └───────────────────────────────────────┘
        │ │ │ │ │ │ │ │
        │ │ │ │ │ │ │ │
        V V V V V V V V
regeneration board 6 failure	1
regeneration board 5 failure	1
regeneration board 4 failure	1
regeneration board 3 failure	1
regeneration board 2 failure	1
regeneration board 1 failure	1
regeneration system warning	1
brake interlock override for AUX	1
        ┌───────────────────────────────────────┐
        │ 07 06 05 04 03 02 01 00 │
        └───────────────────────────────────────┘
        │ │ │ │ │ │ │ │
        │ │ │ │ │ │ │ │
        V V V V V V V V
motor 8	1
motor 7	1
motor 6	1
motor 5	1
motor 4	1
motor 3	1
motor/group 2	1
motor/group 1	1
Notes:
-	A set bit selects the motor/motor group to be switched off.
-	Only one bit may be set at a time.
-	Bits 2...7 apply for GD only.
Axis Status
        ┌───────────────────────────────────────┐
        │ 15 14 13 12 11 10 09 08 │
        └───────────────────────────────────────┘
        │ │ │ │ │ │ │ │
        │ │ │ │ │ │ │ │
        V V V V V V V V
brake released	1
cable car interlock active	1
emergency limit	1
pos. limit	1
pos. pre-limit	1
operating range	1
neg. pre-limit	1
neg. limit	1
        ┌───────────────────────────────────────┐
        │ 07 06 05 04 03 02 01 00 │
        └───────────────────────────────────────┘
        │ │ │ │ │ │ │ │
        │ │ │ │ │ │ │ │
        V V V V V V V V
brake failure	1
encoder failure	1
motor overtemp.	1
runaway	1
drive enable	1
failure encoder 2 [4]	1
failure encoder 14	1
servo failure	1
[4] Az only
Amplifier Status
        ┌───────────────────────────────────────┐
        │ 15 14 13 12 11 10 09 08 │
        └───────────────────────────────────────┘
        │ │ │ │ │ │ │ │
        │ │ │ │ │ │ │ │
        V V V V V V V V
Ampl. 82 not ready	1
Ampl. 82 fault	1
Ampl. 81 not ready	1
Ampl. 81 fault	1
Ampl. 42 not ready	1
Ampl. 42 fault	1
Ampl. 41 not ready	1
Ampl. 41 fault	1
        ┌───────────────────────────────────────┐
        │ 07 06 05 04 03 02 01 00 │
        └───────────────────────────────────────┘
        │ │ │ │ │ │ │ │
        │ │ │ │ │ │ │ │
        V V V V V V V V
Ampl. 52 not ready	1
Ampl. 52 fault	1
Ampl. 51 not ready	1
Ampl. 51 fault	1
Ampl. 12 not ready	1
Ampl. 12 fault	1
Ampl. 11 not ready	1
Ampl. 11 fault	1
Motor Status
Bits 8...15: always zero
        ┌───────────────────────────────────────┐
        │ 07 06 05 04 03 02 01 00 │
        └───────────────────────────────────────┘
        │ │ │ │ │ │ │ │
        │ │ │ │ │ │ │ │
        V V V V V V V V
motor 82 overtemp.	1
motor 81 overtemp	1
motor 42 overtemp	1
motor 41 overtemp	1
motor 52 overtemp	1
motor 51 overtemp	1
motor 12 overtemp	1
motor 11 overtemp	1
Equipment Status

        ┌───────────────────────────────────────┐
        │ 15 14 13 12 11 10 09 08 │
        └───────────────────────────────────────┘
│ 0 0 │ 0 0 0 0
│ │
V V
Pendulum alarm
  / collision switch [5]	1
local axis disable	1
        ┌───────────────────────────────────────┐
        │ 07 06 05 04 03 02 01 00 │
        └───────────────────────────────────────┘
        │ │ │ │ │ │ │ │
        │ │ │ │ │ │ │ │
        V V V V V V V V
fault brakes group 2	1
fault brakes group 1	1
DC bus 2 fault	1
DC bus 1 fault	1
main contactor 2 on	1
main contactor 1 on	1
power supply 2 fault	1
power supply 1 fault	1
[5] Az: pendulum alarm, GD/CH: collision switch encountered
Rate
Integer values for commanded velocity
Max. values:	Az	±4170 * 10-4 °/s = 25 °/min
GD, CH	±417 * 10-4 °/s = 2.5 °/min
Position
Integer values for commanded/actual position
Max. values:	Az	±3,600,000 * 10-4 ° = ± 360 °
GD, CH	0 ... 200,000 * 10-4 ° = 0 ... 20 °
Clear Stack Command
integer "1"	clear stack
any other value	no activity
Watchdog
always integer "20"
Input / Output Status Bytes n, n+1
        ┌───────────────────────────────────────┐
        │ 15 14 13 12 11 10 09 08 │
        └───────────────────────────────────────┘
        │ │ │ │ │ │ │ │
        │ │ │ │ │ │ │ │
        V V V V V V V V
Byte n bits	7 6 5 4 3 2 1 0
        ┌───────────────────────────────────────┐
        │ 07 06 05 04 03 02 01 00 │
        └───────────────────────────────────────┘
        │ │ │ │ │ │ │ │
        │ │ │ │ │ │ │ │
        V V V V V V V V
Byte n+1 bits	7 6 5 4 3 2 1 0
# 3. Interface to PCU
## 3.1. Hardware
at PLC:	CP 524
at PCU:	Becker UCU
interface type	TTY 20 mA

## 3.2. Transfer Requirements
transfer speed:	9600 Bd
no. of data bits:	8
no of stop bits	1
parity	none
transfer PCU --> PLC	every 100 ms (if PCU is plugged in)
transfer PLC --> PCU	once after each transmission by PCU

## 3.3. Description of Protocols
### 3.3.1. From PCU to PLC
Only one type of protocol is sent.

Word-No. Contents hex.
       ┌──────────────────────────────────┐
1 │ start word │ AA55
       │==================================│
2 │ mode selection │
       │==================================│
3 │ function selection │
       │==================================│
4 │ rate potentiometer │
       │==================================│
5 │ Checksum │
       │==================================│
6 │ end word │ 0303
       └──────────────────────────────────┘
### 3.3.2. From PLC to PCU
Only one type of protocol is sent.

Word-No. Contents hex.
       ┌──────────────────────────────────┐
1 │ start word │ BB66
       │==================================│
2 │ LED status │
       │==================================│
3 │ actual current │
       │==================================│
4 │ actual position I │
       │==================================│
5 │ actual position II │
       │==================================│
6 │ checksum │
       │==================================│
7 │ end word │ 0303
       └──────────────────────────────────┘

## 3.4. Data Format
Data transfer is done word by word; one word contains 2 bytes, i.e. 16 bit. The high-byte is always sent first.
The MSB ist set in all data words.
Start word	e.g. AA55, see a.m. protocol definition
End word	0303H
Checksum	sum of all data words
(incl. start word, without end word)
The individual words - disregarding their meaning - will be added as 16 bit integer values with the MSB representing the sign (1=negative). Negative values will be considered as two's complement numbers.
The lower 16 bits of the sum of all data will be transferred as "checksum". Bit 15 and 07 - i.e. the MSBs of both bytes - will always be set; i.e. the checksum will be masked with 8080H.
Mode Selection
        ┌───────────────────────────────────────┐
        │ 15 14 13 12 11 10 09 08 │
        └───────────────────────────────────────┘
        1 │ 0 0 0 0 0 0
        │
        │
        V
Emergency off	1
        ┌───────────────────────────────────────┐
        │ 07 06 05 04 03 02 01 00 │
        └───────────────────────────────────────┘
        0 0 0 0 0 │ │ │
        │ │ │
        │ │ │
        V V V
Carriage House	1
Greg. Dome	1
Azimuth	1
Note:
Only one bit in the mode selection word may be set.
Function Selection
Bit 15: "1"
Bit 8-14: "0"
        ┌───────────────────────────────────────┐
        │ 07 06 05 04 03 02 01 00 │
        └───────────────────────────────────────┘
        │ 0 │ │ 0 0 │ │
        V │ │ │ │
reset	1 V V │ │
move command "ready"	1 0 │ │
move command "go"	0 1 V V
drive off	1 0
drive on	0 1
LED Status
        ┌───────────────────────────────────────┐
        │ 15 14 13 12 11 10 09 08 │
        └───────────────────────────────────────┘
        1 │ │ │ 0 0 │ │
        │ │ │ │ │
        │ │ │ │ │
        V V V V V
PCU inactive[1]	1
ready	1
go	1
drive off	1
drive on	1
        ┌───────────────────────────────────────┐
        │ 07 06 05 04 03 02 01 00 │
        └───────────────────────────────────────┘
        │ │ │ │ │
        │ │ │ │ │
        │ │ │ │ │
        V V V V V
prelimit up/cw	1
prelimit down/ccw	1
limit up/cw	1
limit down/ccw	1
servo failure	1
[1] 24V LED flashing
Current,	bits 0...13:	14 bit integer value
Rate Potentiometer	as multiple of 0.1 %
bit 14:sign (1=negative)
Bit 15 (MSB):	always 1
data range:	0...100.0%
Position
Word I	14 bit integer value
as multiple of 1.000°
bit 0...13:	data bits
bit 14:	sign (1=negative)
bit 15 (MSB):	always "1"
Word II	14 bit integer value
as multiple of 0.0001°
bit 0...13:	data bits
bit 15 (MSB):	always "1"