ARECIBO OBSERVATORY
SERVO DRIVE SYSTEM UPGRADE
Programmable Logic Controller
Simatic S5 - 135U
LIST OF PLC ROUTINES

Software No. S1095034C-2.1
December 1999

Vertex Antennentechnik GmbH
Baumstr. 50
47198 Duisburg
Germany
Tel. +49-2066-2096-0; Fax -11
Contents

# 1. Program Organization
## 1.1. Routine Types

══════════════════════════════════════════════════════════════════

Organization	)
Time driven interrupts	)-- OB ...
Special functions	)

Subreflector control	PB ...; FB ...; FX ...

Data blocks	DB ...; DX ...

══════════════════════════════════════════════════════════════════

## 1.2. Software Organization Overview

PB	FB, FX	DB
------------------------------------------------------------------
General functions	10- 49	180-255	10-49

supervisory functions	10- 19
displays + control panels	20- 29

------------------------------------------------------------------
positions	50- 99	200-255	50- 99
------------------------------------------------------------------
operation	100-149	180-200	100-149
------------------------------------------------------------------
drives	150-199	210-229	150-199
------------------------------------------------------------------
interfaces	220-255	230-239	220-255
------------------------------------------------------------------
library functions	1-179
------------------------------------------------------------------
# 2. List of Routines

## 2.1. Organization Blocks

══════════════════════════════════════════════════════════════════

Program organization	OB 1

──────────────────────────────────────────────────────────────────

Interrupt routine

OB 2

──────────────────────────────────────────────────────────────────

Time driven interrupts	OB 10	called every 10 ms
OB 11	called every 20 ms
OB 10... OB 18	OB 12	called every 50 ms
OB 13	called every 100ms
OB 16	called every 1 s

──────────────────────────────────────────────────────────────────

Special events	OB 20	cold restart
OB 21	manual warm restart
OB 20 ... OB 22	OB 22	power-up
OB 31	internal time out

──────────────────────────────────────────────────────────────────

Integrated special functions	OB 152	cycle time statistics
OB 180	variable DB access
OB 182	copy DWs
OB 190	transfer flags into DWs
OB 191	transfer DWs into flags
OB 220	sign extension
OB 221	set main loop timeout

──────────────────────────────────────────────────────────────────

## 2.2. Program Blocks

══════════════════════════════════════════════════════════════════

General Functions

PB 10 ... PB 49

Supervisory functions	PB 10	control locations & general faults
PB 10 ... PB 19	PB 11	general functions

PB 15	emergency off
-------------------------------------------------------------

Displays and Panels
PB 20 ... PB 29	PB 21	Portable Control Unit

──────────────────────────────────────────────────────────────────

Positions

PB 50 ... PB 99

Position evaluation	PB 50	evaluation of positions (interrupt)
PB 50 ... PB 59	PB 51	read positions
PB 52	encoder selection & supervision
PB 53	limits
PB 54	encoder preset

──────────────────────────────────────────────────────────────────

Operation

PB 100 ... PB 149

General functions	PB 100	general functions during op.
PB 100 ... PB 109	PB 102	signals & horns
PB 109	brake release supervision

-------------------------------------------------------------

Modes	PB 110	Program Track
PB 110 ... PB 119	PB 111	Stow

──────────────────────────────────────────────────────────────────

Program Blocks (cont'd)
══════════════════════════════════════════════════════════════════

Drives

PB 150 ... PB 199

Azimuth Drives	PB 150	release / faults
PB 150 ... PB 159	PB 151	drive functions
PB 152	switch off all drives
PB 153	local functions
PB 154	computer mode
PB 155	brakes
PB 156	cable car interlocks

-------------------------------------------------------------

Gregorian Dome	PB 160	release / faults
PB 160 ... PB 169	PB 161	drive functions
PB 162	switch off all drives
PB 163	local functions
PB 164	computer mode
PB 165	brakes
PB 166	regeneration failures

-------------------------------------------------------------

Carriage House	PB 170	release / faults
PB 170 ... PB 179	PB 171	drive functions
PB 172	switch off all drives
PB 173	local functions
PB 174	computer mode
PB 175	brakes

──────────────────────────────────────────────────────────────────

Interfaces

PB 220 ... PB 239

CP 581	PB 220	interface to CP 581
PB 220 ... PB 229	PB 221	transfer data to CP581 (interrupt)
PB 222	receive data from CP581 (interrupt)
PB 223	communication with CP581

──────────────────────────────────────────────────────────────────
## 2.3. Function Blocks

══════════════════════════════════════════════════════════════════

Library functions[1]
[1] no listing available

FB 1 ... FB 179

General functions	FB 50	intermittent light generator
FB 50 ... FB 59	FB 51	clear DB
FB 52	copy DWs
FB 59	idle block
-------------------------------------------------------------

Control functions	FB 61	parameters for setpoint limiter
FB 60 ... FB 99	FB 62	PI controller
FB 64	loop reset
FB 66	setpoint limiter
FB 68	velocity ramp generator

-------------------------------------------------------------

Handling Blocks	FB 120	SEND
FB 120 ... FB 127	FB 121	RECEIVE
FB 123	CONTROL
FB 124	RESET
FB 125	SYNCHRON
FB 126	SEND-ALL
FB 127	RECEIVE-ALL
-------------------------------------------------------------

Encoder Evaluation Module	FB 130	initialization
FB 130 ... FB 137	FB 131	readout
FB 133	DB check

-------------------------------------------------------------

Communication
FB 160 ... FB 179	FB 173	checksum

──────────────────────────────────────────────────────────────────

Function Blocks (cont'd)
══════════════════════════════════════════════════════════════════

User Blocks

FB 180 ... FB 255, FX 0 ... FX 255

Operation	FB 180	Rate mode control loops
FB 180 ... FB 189	FB 181	Preset mode control lops
FB 182	Program Track control lops
FB 184	no operation control
FB 186	Program Track control
FB 187	Program Track start-up
-------------------------------------------------------------

Aux. arithmetic functions	FB 190	absolute difference
FB 190 ... FB 199	FB 191	evaluate next stack data set
FB 192	Program Track stack search
FB 193	potentiometer hysteresis
FB 194	Program Track ramp
FB 195	position increment calculation
FB 196	velocity feedforward
FB 198	byte check
FB 199	position limit check
-------------------------------------------------------------

Internal functions	FB 200	general functions
FB 200 ... FB 209	FB 201	lamp test
FB 207	cold restart functions
FB 208	reset automatic functions
FB 209	start-up functions
-------------------------------------------------------------

Drive functions	FB 210	drive control
FB 210 ... FB 219	FB 211	prepare inputs for drive control
FX 210 ... FX 219	FB 212	Az bending
FB 213	gravity compensation
FB 214	torque bias
FB 215	drive to stow
FB 216	limits
FB 217	motor heating
FB 218	GD-CH interlock
FB 219	cable car interlock limits

-------------------------------------------------------------

Function Blocks (cont'd)
══════════════════════════════════════════════════════════════════

Aux. functions	FB 220	evaluate positions
FB 220 ... FB 229	FB 221	read positions
FB 222	cycle time measurement
FB 223	load loop parameters
FB 224	CH gravity compensation in Aux
FB 225	drive standstill after Preset
FB 226	encoder readout failure handling
FB 227	auxiliary flags
FB 229	time synchronization

-------------------------------------------------------------

Interfaces	FB 230	positions for CP581
FB 230 ... FB 239	FB 231	evaluate data from CP581
FB 232	evaluate data from PCU
FB 233	prepare data for PCU
FB 234	axis related PCU data
FB 235	pepare data for SRC
FB 236	axis command evaluation

-------------------------------------------------------------

Monitoring functions	FB 250	analog test outputs
FB 250 ... FB 255

──────────────────────────────────────────────────────────────────
## 2.4. Data Blocks

Data blocks (DB,DX) must not be loaded into an Eprom module unless otherwise noted!
All data blocks except those in the Eprom will be generated automatically after a cold restart.
══════════════════════════════════════════════════════════════════
System Data Blocks[2]
[2] do not modify!

DB 0; DB 1; DX 0	DB 0	block address list
DB 1	periphery allocation
DX 0	system parameters3

──────────────────────────────────────────────────────────────────
User Data Blocks

General functions	DB 10	test
DB 10 ... DB 49	DB 11	time
DB 12	flag memory
DB 21	PCU

-------------------------------------------------------------

Positions	DB 50	Positions
DB 50 ... DB 99	DB 51	requ'd by FB130

DB 99	requ'd by FB52
-------------------------------------------------------------

Drives and Operation	DB 150	drive data general / Az
DB 100 ... DB 199	DB 151	drive system default parameters[3]
[3] to be loaded into EPROM

DB 160	drive data GD
DB 170	drive data CH

DB 180	control loop standard parameters3
DB 181	control loop parameters Az
DB 182	control loop parameters GD
DB 183	control loop parameters CH
DB 184	control loop parameters bending
DB 189	control loop auxiliary DB

-------------------------------------------------------------

Interfaces	DB 221	data for CP581
DB 220 ... DB 239	DB 222	data from CP581
DB 223	program track data
DB 224	program track aux. DB

-------------------------------------------------------------

Monitoring	DB 250	analog test outputs
DB 240 ... DB 255

──────────────────────────────────────────────────────────────────